| Version | Date | Description of Revisions |
| --- | --- | --- |
| 1 | April 12, 2016 | New Specification (AAM) |

NOTE:

This is a CONTROLLED Document. Any documents appearing in paper form are not controlled and should be checked against the on-line file version prior to use.

Notice: This Document hardcopy must be used for reference purpose only.

The on-line copy is the current version of the document.

# GENERAL

## Related Sections

### Under "Related Sections", identify other Sections that are related to, and/or dependent on, the work results or information specified elsewhere.  The list should be limited to Sections with specific information that the reader might expect to find in this Section, but is specified elsewhere.  For example, if hardware for aluminum entrances is specified in the aluminum entrance Section, a cross-reference would be appropriate in the finish hardware Section.  The purpose of this cross-referencing is for information only, to aid in finding those other requirements—not to define the scope of the Section.

### Cross-referencing here may also be used to coordinate assemblies or systems whose components may span multiple Sections and which must meet certain performance requirements as an assembly or system.

### Contractor is responsible for coordination of the Work.

### This Section is to be completed/updated during the design development by the Consultant. If it is not applicable to the section for the specific project it may be deleted.]

### [List Sections specifying related requirements.]

### Section [______ – ____________]:  [Optional short phrase indicating relationship].

#### Section 01300 – Submittals

#### Section 05120 – Structural Steel

#### Section 05500 – Metal Fabrications – General.

#### Section 05501 – Metal Fabrications – Architectural

#### Section 05502 – Metal Fabrications – Structural.

#### Section 05503 – Metal Fabrications – Mechanical

#### Section 05510 – Metal Stairs

#### Section 05512 – Aluminum Handrails

## References

### The "Code of Standard Practice for Structural Steel for Buildings, 7th Edition, 2009" of the CISC shall govern this work except as otherwise noted on drawings or in specifications.

### The following is a list of standards which may be referenced in this Section:

#### Canadian Standard Association (CSA):

##### CAN/CSA W117.2-12, Safety in Welding, Cutting, Allied Processes.

##### CAN/CSA W178.2-14, Certification of Welding Inspectors

##### CAN/CSA W186-M1990 (R2012), Welding of Reinforcing Bars in Reinforced Concrete Construction.

##### CAN/CSA W47.1-09 (R2014) Certification of Companies for Fusion Welding of Steel

##### CAN/CSA W47.2-11 (R2015), Certification of Companies for Fusion Welding of Aluminum

##### CAN/CSA W48-14 Filler Metals and Allied Materials for Metal Arc Welding

##### CAN/CSA W55.3-08 (R2013), Certification of Companies for Resistance Welding of Steel and Aluminum

##### CAN/CSA W59.2-M1991 (R2103), Welded Aluminum Construction.

##### CAN/CSA W59-13 Welded Steel Construction (Metal Arc Welding).

##### CAN/CSA G30.18-09 (R2014), Carbon Steel Bars for Concrete Reinforcement.

#### ASTM International (ASTM):

##### ASTM A370-15, Standard Test Methods and Definitions for Mechanical Testing of Steel Products.

##### ASTM E10-15a, Standard Test Method for Brinell Hardness of Metallic Materials.

##### ASTM E23-12c, Standard Test Methods for Notched Bar Impact Testing of Metallic Materials.

#### American Welding Society (AWS):

##### AWS D1.1/D1.1M:2015, Structural Welding Code - Steel.

##### AWS A2.4:2012 Standard Symbols for Welding, Brazing and  Nondestructive Examination

#### Canadian General Standards Board (CGSB):

##### CAN/CGSB 48.9712-2014/ISO 9712:2012, IDT, Non-Destructive Testing – Qualification and Certification of NDT Personnel.

#### American Society of Mechanical Engineers (ASME):

##### ASME BPVC-V- 2015 Section V, Nondestructive Examination.

##### ASME BPVC-IX- 2015 Section IX, Welding, Brazing and Fusing Qualifications

## Measurement and Payment

### The Vendor shall include all costs for all labour, equipment, and materials within the appropriate unit price items included within the Schedule of Unit Prices. No separate payment shall be made.

## Definitions

### Class W47.1 welding positions flat (F) horizontal (H); vertical (V) overhead (O).

### BPV: Boiler and Pressure Vessel

### BPVC: Boiler and Pressure Vessel Code

### CJP: Complete Joint Penetration.

### CWB: Canadian Welding Bureau.

### CWI: Certified Welding Inspector.

### GTSM: Gauge to Sound Metal.

### MT: Magnetic Particle Testing.

### NDE: Nondestructive Examination.

### NDT: Nondestructive Testing.

### PJP: Partial Joint Penetration.

### PQR: Procedure Qualification Record.

### PT: Liquid Penetrant Testing.

### RT: Radiographic Testing.

### UT: Ultrasonic Testing.

### VT: Visual Testing.

### WPQ: Welding Personnel Performance Qualification.

### WPS: Welding Procedure Specification.

### WPDS: Welding Procedure Data Sheets.

### WQR: Welder Qualification Record.

## Submittals

### Representative Welding Data on Shop and Field drawings:

#### Show on a weld map the complete information regarding base metal specification designation, location, type, size, and extent of welds with reference to WPS and NDE numbers in the tail of the welding symbol.

#### Distinguish between shop and field welds.

#### Indicate, by welding symbols or sketches, details of welded joints and preparation of base metal. Provide complete joint welding details showing bevels, groove angles, and root openings for welds.

#### Fillet weld symbols shall show fillet size and length.

#### Groove weld symbols shall indicate CJP or PJP or GTSM in the tail of the symbol, as applicable.

#### For pipe fittings, provide a joint weld beveling diagram.

#### Welding and NDE symbols shall be in accordance with AWS A2.4.

#### Welding terms and definitions shall be in accordance with AWS A3.0.

#### Submit welding data together with applicable shop drawings as a complete package.

### Informational Submittals:

#### The following information shall be submitted whenever a request is made. This information shall be readily available for the inspectors employed by the Region’s Independent testing agency.

##### When CAN/CSA applies, WPS’s and related WPDS’s shall be available for all joints prequalified in accordance with W59. Similar documentation is required for non-prequalified joints accompanied by PQR’s for the non-prequalified joints. All such documentation shall be affixed with the CWB acceptance stamp.

##### When AWS applies, WPS’s standard formats shall be available for all prequalified and non-prequalified joints. In addition, PQR’s shall be documented for non-prequalified joints.

##### When the Boiler and Pressure Vessel Code BPVC applies, WPS’s and PQR’s shall be available in accordance with ASME BPVC SECT. IX approved by the authority having jurisdiction.

##### When CAN/CSA W55.3 applies, documentation of resistance welded joint qualification accepted by the CWB shall be available.

## Qualifications

### Structural fabricators and erectors shall be certified in accordance with CAN/CSA W47.1 and/or W47.2.

### BPVC fabricators shall be qualified in accordance with ASME BPVC Section IX.

### Welding personnel shall be qualified in accordance with the following codes: CAN/CSA W47.1 or W47.2; AWS D1.1; D1.2; D1.6; ASME Section IX.

### Inspection Agencies shall be qualified in accordance with CAN/CSA W178.2 and individual non-destructive inspection personnel shall be qualified in accordance with the appropriate CAN/CGSB requirements.

## Quality Control

### Source Quality Control

#### The Contractor’s CWI shall be present whenever shop welding is to be performed. The inspector shall record a report on the quality of Work regarding compliance or non-compliance with the CSA codes CAN/CSA W59, CAN/CSA W59.2 and/or the Contract Documents. Repairs, corrective action or rejection shall be at the discretion of the Consultant, not the inspector. Visual inspection shall be performed by the inspector on all shop and/or field welds to verify that:

##### Specified and properly qualified, or prequalified welding procedures are used and that welding is performed in accordance with those procedures.

##### Only specified base materials and welding consumables are used and that welding consumables are stored and maintained in proper condition for use as specified in the Contract Documents.

##### Welders, welding operators and tackers are properly qualified and that their qualifications permit them to use the processes specified in the Contract Documents.

##### Joint preparation and fit-up meet the requirements of the welding procedures and the Drawings, prior to welding.

##### Preheat and interpass temperatures are in accordance with the Specifications, or at a minimum, Table 503 of CAN/CSA W59.

##### Size, length, number and location of welds conform to the shop or field drawings (random check only).

### Field Quality Control

#### The Contractor’s CWI shall be present whenever field welding is to be performed. Inspection shall be in accordance with subsection 1.6.1 – Source Quality Control as it applies to field welds.

### CWI duties include:

#### Inspection prior to assembly, during assembly, during welding, and after welding.

#### Verifying conformance of specified job material and proper storage.

#### Monitoring conformance of WPS.

#### Monitoring conformance of WPQ.

#### Inspecting weld joint fit-up and in-process inspection.

#### Providing 100 percent visual inspection of all welds.

#### Supervising nondestructive testing personnel and evaluating test results.

#### Maintaining records and preparing a report confirming that the results of inspections and testing comply with the requirements of the Contract Documents.

### Inspection:

#### The Region will retain an independent testing agency for checking weld quality as specified in the related Sections listed in subsection 1.1.

## Sequencing and Scheduling

### Unless otherwise specified the Contract Documents., all submittals required in this Section shall be submitted and approved prior to commencement of welding operations.

# PRODUCTS (Not used)

# EXECUTION

## General

### Welding and Fabrication by Welding: Conform to governing welding codes referenced in the attached Welding and Nondestructive Testing Table.

## Nondestructive Weld Testing Requirements

### See below for table

| Specification Section | Governing Welding Codes or Standards | Submit Written NDT Procedure Specifications | NDT Requirements |
| --- | --- | --- | --- |
| 15200 Piping Systems | See Section 15200 for governing welding codes and standards. | Yes | 100% VT; See Section 15200 for additional NDT requirements. |
| 03210 Reinforcing Steel | CAN/CSA W186, Welding of Reinforced Bar in Reinforced Concrete Construction | Yes | 100% MT of all rebar splices; see Section 03210 |
| 05500 Metal Fabrications (Basic) | CAN/CSA W59, Welded Steel Construction (Metal Arc Welding)or CAN/CSA W59.2, Welded Aluminum Construction | Yes | 100% VT; see Section 05500 |
| 05510 Aluminum Guards and Handrails | CAN/CSA W59.2, Welded Aluminum Construction | No | 100% VT; see Section 05512 |

## Weld Defect Repair

### Repair and retest rejectable weld defects until sound weld metal has been deposited in accordance with the appropriate welding codes referred to above.

### Repair and retest rejectable weld defects to meet the design and/or the Contract Drawings and Specifications. Retesting shall be performed with the same NDT method used for the initial tests and to the same frequency of testing.

END OF SECTION